## Cover
احداث نیروگاه خورشیدی 20 مگاواتی زارچ یزد PKSP-P2-C2-0410
20 MW Zarch Solar Power Plant Project
Document Title: |  |  | ITP for Inverter
ITP for Inverter
`
01 | 2026/06/09 | IFA |  | M. Milan | H. Goudarzi | H. Goudarzi
00 | 2026/06/01 | IFC |  | M. Milan | H. Goudarzi | H. Goudarzi
Rev. | Date | Purpose of Issue |  | Prepared By | Checked By | Approved By

## Rev
احداث نیروگاه خورشیدی 20 مگاواتی زارچ یزد PKSP-P2-C2-0410
20 MW Zarch Solar Power Plant Project
Document Title: |  |  |  |  | ITP for Inverter
Tabulation of Revised Page
| Sheet | Revisions | [10 empty] | Sheet | Revisions
|  | 00 | 01 | 02 |  | 03 | 04 | 05 | 06 | 07 | 08 | 09 |  | 00 | 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09
| 1 | V | V | [9 empty] | 41
| 2 | V | V | [9 empty] | 42
| 3 | V | V | [9 empty] | 43
| 4 | V | V | [9 empty] | 44
| 5 | V | V | [9 empty] | 45
| 6 | V | V | [9 empty] | 46
| 7 | [11 empty] | 47
| 8 | [11 empty] | 48
| 9 | [11 empty] | 49
| 10 | [11 empty] | 50
| 11 | [11 empty] | 51
| 12 | [11 empty] | 52
| 13 | [11 empty] | 53
| 14 | [11 empty] | 54
| 15 | [11 empty] | 55
| 16 | [11 empty] | 56
| 17 | [11 empty] | 57
| 18 | [11 empty] | 58
| 19 | [11 empty] | 59
| 20 | [11 empty] | 60
| 21 | [11 empty] | 61
| 22 | [11 empty] | 62
| 23 | [11 empty] | 63
| 24 | [11 empty] | 64
| 25 | [11 empty] | 65
| 26 | [11 empty] | 66
| 27 | [11 empty] | 67
| 28 | [11 empty] | 68
| 29 | [11 empty] | 69
| 30 | [11 empty] | 70
| 31 | [11 empty] | 71
| 32 | [11 empty] | 72
| 33 | [11 empty] | 73
| 34 | [11 empty] | 74
| 35 | [11 empty] | 75
| 36 | [11 empty] | 76
| 37 | [11 empty] | 77
| 38 | [11 empty] | 78
| 39 | [11 empty] | 79
| 40 | [11 empty] | 80

## Act
احداث نیروگاه خورشیدی 20 مگاواتی زارچ یزد PKSP-P2-C2-0410
20 MW Zarch Solar Power Plant Project
Document Title: |  |  |  | ITP for Inverter
1. Purpose
The purpose of this inspection and test plan is to establish the inspections and tests in conjunction with quality plan for inverter production.
2. Definitions
Project: Construction of the 20 MW solar power plant in Zarch, Yazd
|  | OW | Employer: PKSPCO
|  | SP | Site Supervision :
|  | CO | EPC Contractor: Pishgaman Energy Nouratech
|  | H | Hold point (Notification required, Presence is mandatory)
|  | W | Witness (Notification required, Presence not mandatory)
|  | RC | Random Check (Notification required, Presence not mandatory)
|  | RD | Review of Documents
|  | A | Approved
|  | SW | Spot Witness (Notification required, Presence not mandatory)
3. References
Codes and standards for inspections and tests should be in accordance with those specified in the contractual documents, purchase orders, requisitions, specifications, data sheets, drawings and company official instructions. Applicable Standards: Grid connection standard EN50549, G99, AS4777.2, VDE0126, IEC61727, VDE4110, CEA 2019 Safety / EMC standard IEC62109-1/-2, EN61000-6-2/-4 (if applicable)
4.Responsibilities
Contractor shall prepare inspection procedure and submit for review and approval of Company prior to use.
The contractor shall control the individual inspection procedures for final inspection. The record means work instructions, checklists which give evidence that the work has passed inspection.

## ITP 1
احداث نیروگاه خورشیدی 20 مگاواتی زارچ یزد PKSP-P2-C2-0410
20 MW Zarch Solar Power Plant Project
Document Title: |  |  | ITP for Inverter
Inspection and test plan (ITP)
| Row | Step of inspection / Activity |  | Reference | Standard Renge | ACCEPTANCE CRITERIA) | inspection position |  |  | Note
|  |  |  | procedure /spec/code |  |  | NT | THP | PKSP
| 1 | Inspection
| 1.1 | Check the surface—clean and no scratch; check the LCD Board—no scratch; |  | Appearance inspection standards | Refer to the finished product appearance inspection standard | Fully compliant | W | W | RD
| 1.2 | Check and confirm the tightness of screws; |  | 1. The Biotechnology Department creates Standard Operating Procedures (SOPs) based on the torque standards provided by R&D, defining torque standards for different screws. 2. The Engineering Department (ME) provides manual torque screwdrivers that meet the torque specifications to the Industrial Quality Control (IPQC) department for random inspection and verification, based on the torque values ​​defined in the SOPs. 3. Frequency: IPQC inspects 5 pieces every 2 hours to confirm whether the screws are tightened. | Refer to the SOP (Standard Operating Procedure) process inspection checklist | Valid & approved | W | W | RD
| 1.3 | Check and confirm the tightness of AC/DC terminal; |  | 1. The Biotechnology Department creates Standard Operating Procedures (SOPs) based on the torque standards provided by R&D, defining torque standards for different screws. 2. The Manufacturing Equipment (ME) department sets the electric screwdriver torque according to the torque values ​​defined in the SOPs and performs morning and afternoon checks to confirm whether the electric screwdriver torque is up to standard. 3. The Industrial Quality Control (IPQC) department conducts visual inspections at 5 pieces per 2 hours to confirm whether the screws are tightened. | Refer to the SOP (Standard Operating Procedure) process inspection checklist | Valid & approved | W | W | RD
| 1.4 | Check the silk print—clear, in proper place, and with correct color; |  | Printing: Refer to the drawings; Inspection: Refer to the screen printing inspection specifications. | Screen Printing Inspection Standards | Valid & approved | W | W | RD
| 1.5 | Check the package—no humidity, subsidence, or smearing; |  | Reference Packaging Specifications | Refer to the finished product appearance inspection standard | Valid & approved | W | W | RD
| 1.6 | Check the silk print (on package)—confirm to the design drawing; |  | Reference Packaging Specifications | Refer to the finished product appearance inspection standard | Valid & approved | W | W | RD
| 1.7 | Check the accessories are complete, the nameplate is correct, and the entity is in accordance with the order requirement. |  | Refer to the work order BOM and drawings | Meet the relevant requirements | Valid & approved | W | W | RD
| 2 | Safety Test items |  |  |  | Q06-001-COW-03 | H | RC
| 2.1 | Hi-pot/PV isolation/ Ground resistance test |  | 2545Vdc(Pv/Grid)to-Ground. 5090Vdc(PW/Grid)to-RS485. | No-breakdown.arc·or sparksu | Valid & approved | W | W | RD
| 2.2 | Sealing test |  | One endotracheal tube is connected, and all others are closed and sealed, with all interfaces properly plugged. | -3200 | Valid & approved | W | W | RD
| 2.3 | Power up test |  | Refer to power-on test requirements | The equipment is operating normally after power-on. | Valid & approved | W | W | RD
| 3 | Funtional Test items
| 3.1 | Night consumption |  | The inverter's DC side is disconnected, and the AC side is connected to the grid. A power meter measures the AC side power. | ＜3W | Valid & approved | W | W | RD
| 3.2 | Start up voltage |  | Measure standby power consumption when supplied by AC | ＜500V | Valid & approved | W | W | RD
| 3.3 | Comm. Test |  | Tested under rated power | The communication is normal | Valid & approved | W | W | RD
| 3.4 | Display Accuracy calibration |  | After the external equipment conditions stabilize (3-5 seconds after adjustment), simultaneously record the voltage/current/frequency/output power of phases A, B, and C displayed on the LCD, and the voltage/current/frequency/output power of phases A, B, and C measured by power metering. Calculate the differences, and judge the results based on the absolute difference. | Voltage: (LCD display - power meter display), error value ±8V); Current: LCD display - power meter display ≤1%, ±8A; Frequency: LCD display - power meter display <0.05Hz; | Valid & approved | W | W | RD
| 3.5 | TEMP Test |  | Temperature detection | 17-45° | Valid & approved | W | W | RD
| 3.6 | Fan Test |  | Fan self-test enabled test | Determine whether the fan start-stop operation status is qualified. | Valid & approved | W | W | RD
| 3.7 | Max.MPPT Efficiency |  | NA | NA | Valid & approved | W | W | RD
| 3.8 | LOW IRRADIANCE TEST |  | NA | NA | Valid & approved | W | W | RD

## ITP2
احداث نیروگاه خورشیدی 20 مگاواتی زارچ یزد PKSP-P2-C2-0410
20 MW Zarch Solar Power Plant Project
Document Title: |  |  | ITP for Inverter
Inspection and test plan (ITP)
| Row | Step of inspection / Activity |  | Reference | Passed Renge | ACCEPTANCE CRITERIA) | inspection position |  |  | Note
|  |  |  | procedure /spec/code |  |  | NT | THP | PKSP
| 3.9 | DC Accuracy calibration |  | Synchronous recording of liquid crystal display PV1, PV2 channels... voltage, current, input power and power measurement test PV1, PV2 channels... voltage, current, input power, and calculating the difference. The results are judged based on the absolute difference. | Voltage: (LCD display - power meter display) / Power meter display * 100% ≤ 1%, ±15V (for data recording, data distribution analysis) Current: LCD display - power meter display ±16A (for data recording, data distribution analysis) | Valid & approved | W | W | RD
| 3.10 | AC Accuracy calibration |  | After the external equipment conditions are stable (after adjustment for 3 to 5 seconds), synchronously record the voltages/current/frequencies/output power of phases A, B, and C displayed on the LCD, as well as the voltages/current/frequencies/output power measured by the power metering test for phases A, B, and C, and calculate the differences. The results will be judged based on the absolute differences. | Voltage: (LCD display - power meter display), error value ±8V); Current: LCD display - power meter display ≤ 1%, ±8A Frequency: LCD display - power meter display < 0.05Hz; | Valid & approved | W | W | RD
| 3.11 | DC/AC power Comparison |  | Synchronously record the LCD input DC power of the inverter and the LCD output AC power of the inverter, calculate the difference, and determine the result based on the absolute difference. | Inverter (LCD input DC power - Inverter LCD output AC power) / LCD input DC power * 100% ≤ 5% | Valid & approved | W | W | RD
| 3.12 | Conversion efficiency |  | The upper computer reads the efficiency of the power analyzer. | 95% < AC power measured by power meter ÷ DC power measured by power meter < 98.5% Average the 10 cumulative data points (1 data point collected every 0.5 seconds) | Valid & approved | W | W | RD
| 3.13 | THDi |  | 1) Set the PV source voltage and power through the ATE system; 2) The loaded inverter starts and operates normally. | THD (total) ≤ 5%; Average of 10 consecutive data points (1 data point collected every 0.5 seconds) | Valid & approved | W | W | RD
| 3.14 | IR and continuity tests passed |  | 1. Connect the analog insulation fault testing tool (with the specified resistance connected), and close the connection. It is required that when the inverter is set to 90% of the company's standard resistance, it cannot be connected to the grid, the LCD fault indicator light remains constantly on, displaying "PV ISO-PRO" fault, and when the inverter is set to 110% of the company's standard resistance, it can be connected to the grid normally. Note that each path needs to be tested through PV+ to ground and PV- to ground. (1) Confirm the type of the inverter and refer to the comparison table to confirm the insulation impedance standard value R for the country or region (such as the standard requirement of 20K) and the company's standard setting value R (such as the company's product setting value of 200K). Connect the DC side of the inverter to the DC power supply, and directly connect the AC side output to the grid (if using an AC source, make sure that the power ground wire and the inverter ground wire are connected to the same large ground). (2) Connect the test ground wire to the grounding terminal of the inverter. (3) According to the confirmed setting value R, prepare the test resistor Rmin (90% of the company's standard setting value R) and connect it between the positive pole (or negative pole) and the grounding terminal of the inverter. (4) First turn on the grid or AC power supply, then start the DC source to power on the inverter. (5) Check if the LCD display of the inverter reports the PV ISO-PRO fault, record it, then disconnect the grid and DC source, switch the test resistor. (6) Connect the confirmed and prepared resistor Rmax (110% of the company's standard setting value R) between the positive pole (or negative pole) and the grounding terminal of the inverter. (7) First turn on the grid or AC power supply, then start the DC source to power on the inverter. (8) Check if the LCD display of the inverter is normal and connected to the grid, and if there is power output, then disconnect the grid and DC source, record the results. 2. PV- to ground, operate in the same way as PV+ to ground. | 1. If the PV ISO-PRO module fails when the minimum接入 resistance Rmin is connected and it can be normally connected when the maximum接入 resistance Rmax is connected, the test meets the standard requirements. 2. If the PV ISO-PRO module does not fail when the minimum接入 resistance Rmin is connected or fails when the maximum接入 resistance Rmax is connected， the test does not meet the standard requirements. | Valid & approved | W | W | RD
| 3.15 | Soft Run |  | 1) Set the PV source voltage and power through the ATE system; 2) The loaded inverter starts and operates normally. | The software starts timing when it receives the "power-on" command. It stops timing when the inverter sends a "running" status feedback. It is considered qualified if the timing duration does not exceed the specified limit (within 100 seconds). | Valid & approved | W | W | RD
| 3.16 | Time Calibration |  | Read the time of the inverter and compare it with the real-time time of the computer. Determine whether the time is within the standard range. | ≤ 5 minutes | Valid & approved | W | W | RD
| 3.17 | Software Version |  | Read the current software version of the inverter and compare it with the configured version of the system settings; 1) Pre-configure all the specifications of the inverters and their corresponding software versions; 2) Conduct communication comparison; | Correct version | Valid & approved | W | W | RD
| 3.18 | SN SN Comparison |  | Match the machine SNs exactly | Match SN consistency | Valid & approved | W | W | RD
| 3.19 | Grounding voltage test |  | 1. If the external DC source and the grid environment impedance are fixed, the reading of Jinlang Cloud's ground voltage value is also a constant value. This can be used to determine whether there is any inconsistency in insulation impedance within the inverter. 2. The upper computer reads the ground voltage value. | Read the value of the liquid crystal grounding voltage within the DC voltage range of 200 - 700V. | Valid & approved | W | W | RD
| 3.20 | Set national standards |  | Set to the national standard that was originally set for this model of device at the time of its manufacture. | Set to the national standard that was originally set for this model of device at the time of its manufacture. | Valid & approved | W | W | RD
| 3.21 | Reset |  | 1. This test will be conducted at the end. 2. The 485 communication is enabled, and a one-click shutdown command is sent (including clearing historical data and restoring factory settings). 3. The operation records and fault records of the inverter have been cleared. | Check the operation records of the inverter. The fault records have been cleared and it has been restored to the factory settings. | Valid & approved | W | W | RD
| 3.22 | PF |  | The upper computer reads the PF value displayed by the power analyzer. | When the Pn ratio is greater than 50% to 100%, 0.99 ≤ λ ≤ 1; When the Pn ratio is between 20% and 50%, 0.95 ≤ λ ≤ 1; Take the average of 10 cumulative data points (collecting data once every 0.5 seconds) | Valid & approved | W | W | RD
| 3.23 | DC Injection |  | The host computer reads the AC and DC components displayed by the power analyzer. | ≤2%; The average value of 10 consecutive data sets is calculated (1 data point is collected every 0.5 seconds) | Valid & approved | W | W | RD

## ITP3
احداث نیروگاه خورشیدی 20 مگاواتی زارچ یزد PKSP-P2-C2-0410
20 MW Zarch Solar Power Plant Project
Document Title: |  |  | ITP for Inverter
Inspection and test plan (ITP)
| Row | Step of inspection / Activity |  | Reference | Passed Renge | ACCEPTANCE CRITERIA) | inspection position |  |  | Note
|  |  |  | procedure /spec/code |  |  | NT | THP | PKSP
| 4 | Document Review
| 4.1 | Datasheet |  | Manufacturer Datasheet | - | Approved | W | W | RD
| 4.2 | User Manual Review |  | Installation, Operation & Maintenance Manual | - | Approved | W | W | RD
| 4.3 | FAT Report Review |  | Factory Acceptance Test Report | - | Valid & approved | W | W | RD
| 4.4 | IEC 62109 Certificate |  | IEC 62109-1, IEC 62109-2 | - | Valid & approved | W | W | RD
| 4.5 | EMC Certificate |  | IEC 61000 Series | - | Valid & approved | W | W | RD
| 4.7 | Grid Compliance Certificate |  | EN50549 Test Report | - | Valid & approved | W | W | RD
| 4.8 | LVRT/HVRT Test Report |  | EN50549 Test Report | - | Valid & approved | W | W | RD
| 4.9 | Reactive Power Capability Report |  | EN50549 Test Report | - | Valid & approved | W | W | RD