Technical Specifications of the Inverter

| NO. | TECHNICAL DESCRIPTION | REQUIREMENTS DATA |
| --- | --- | --- |
| Input (DC) |  |  |
| 1 | Max. Input Voltage | 1500 V |
| 2 | Min input voltage/ Start Voltage | 550 V |
| 3 | Nominal input voltage | 1080 V |
| 4 | Number of MPPT | 12 |
| 5 | Max. number of input per MPPT | 2 |
| 6 | Max. Current per MPPT | 40 A |
| 7 | Max. Short Circuit Current per MPPT | 60 A |
| 8 | MPPT Operating Voltage Range | 500 ~ 1500 V |
| Output (AC) |  |  |
| 9 | Nominal AC Output Power | ≥350 kVA |
| 10 | Max. Output Current | 254 A |
| 11 | Nominal Output Current | 231 A |
| 12 | Nominal Output Voltage | 3/PE , 800 V |
| 12 | AC Voltage Range | 640- 920 V |
| 13 | Rated AC Grid Frequency | 50 Hz |
| 14 | Adjustable Power Factor Range | 0.8 LG ... 0.8 LD |
| Protection |  |  |
| 15 | Smart String-level Disconnection (SSLD) | Yes |
| 16 | Smart Connector-level Detection (SCLD) | Yes |
| 17 | AC Overcurrent Protection | Yes |
| 18 | DC Reverse-polarity Protection | Yes |
| 19 | PV-array String Fault Detection | Yes |
| 20 | DC Surge Arrester | Type II |
| 21 | AC Surge Arrester | Type II |
| 22 | DC Insulation Resistance Detection | Yes |
| 23 | Residual Current Detection Unit | Yes |
| Communication |  |  |
| 24 | Display | LED indicators; WLAN adaptor |
| 25 | USB | Yes |
| 26 | MBUS | Yes |
| 27 | RS485 | Yes |
| General |  |  |
| 28 | Dimensions (W x H x D) | 1136*870*361 |
| 29 | Weight | By vendor |
| 30 | Operating Temperature Range | -30 ~ +60 ºC |
| 31 | Cooling Method | Smart Air Cooling |
| 32 | Max. Operating Altitude without Derating | 4000 m |
| 33 | Relative Humidity | 0 ~ 100% |
| 34 | DC Connector | MC4/ EVO2 connector |
| 35 | AC Connector | OT terminal (max. 400mm2) |
| 36 | Protection Degree | ≥IP66 |
| 37 | Topology | Transformerless |