Technical Specifications of the MV Station

| NO. | TECHNICAL DESCRIPTION | REQUIREMENTS DATA |
| --- | --- | --- |
| Input |  |  |
| 1 | Available Inverters / PCS | Inverters with power ratings exceeding 300 kVA |
| 2 | LV AC Inputs | 10 |
| 3 | LV AC Specification | 260 A/ 800 V |
| 4 | AC Power | 3200 kVA |
| 5 | Rated Input Voltage | 800 V |
| 6 | Max. Input Current at nominal voltage | 2540 A |
| Output |  |  |
| 7 | Rated Output Voltage | 20 kV |
| 8 | Frequency | 50 Hz |
| 9 | LV Main Switches | 4000 A/ 800V/ 1pcs |
| 10 | Transformer Type | Oil-immersed, Conservator Type |
| 11 | Transformer Cooling Type | ONAN |
| 12 | Transformer Tappings | ± 2 x 2.5% |
| 13 | Transformer Oil Type | Mineral oil |
| 14 | Transformer Vector Group | Dy11 |
| 15 | Auxiliary Transformer | Dry Type Transformer ,15 kVA (Optional: 40 kVA) |
| 16 | Auxiliary Transformer Vector Group | Dyn11 |
| 17 | Output Voltage of Auxiliary Transformer | 3/PE , 400 V |
| Protection |  |  |
| 18 | Transformer Detection & Protection | Oil Level, Oil Temperature, Oil Pressure and Buchholz |
| 19 | Protection Degree of MV & LV Room | IP 54 |
| 20 | LV Overvoltage Protection | Type I+II |
| Features |  |  |
| 21 | 2 kVA UPS | Yes |
| 22 | MV Surge Arrester for Transformer | Optional |
| General |  |  |
| 23 | Dimensions (W x H x D) | By Vendor |
| 24 | Weight | By Vendor |
| 25 | Operating Temperature Range | -15°C ~ 50°C |
| 26 | Relative Humidity | 0% ~ 95% |
| 27 | Max. Operating Altitude | 1600 m |
| 28 | LV & MV Room Cooling | Air Condition Unit |
| 29 | Communication | RS485, Ethernet, Optical fiber |